## Introduciton
Unpolished Solar System Reckoner (USSR)
Copyright 2019 Ben Elliston (bje@air.net.au)

Instructions

1. Work through each yellow worksheet from left to right.
2. Enter data into yellow cells.

You may need to enter module or inverter data into the blue worksheets.
You should not need to edit the green worksheets unless adding new locations.

FIXME
There needs to be a worksheet that calculates overcurrent protection requirements.

## Matching
Matching modules to inverter

Location
Melbourne

Inverter model	Min MPPT voltage	Max MPPT voltage	Max input voltage	Max input current	Max DC power	Min MPPT w/ margin	Max MPPT w/ margin	Max input w/ margin	Max output current	Efficiency
SMA SB15000TL	240	800	1000	33	27000	264	760	600	29	98%

Module model	Pmax	Vmp	Imp	Voc	Isc	Efficiency	Fuse / Rating (A)	Pmax	Voc	Vmp	Isc	Manuf. Tolerance	Height	Width	Vmp min	Vmp max	Voc max
TSM-260	260	30.6	8.5	38.2	9	15.9	15	-0.41%	-0.32%	-0.41%	0.05%	0%	1650	941	24.33	34.36	41.87

Voltage		Rounded
Min # modules		11
Max # modules		14
Max # modules (MPPT)		22

Current		Rounded
Max # strings per MPPT	3.67	3

Power		Rounded
Max # modules		103

## Voltage Drops
Minimum cross-sectional area (CSA)

AC CSA for 1% drop			DC CSA for 3% drop
Estimated length	2		Estimated length	8
Resistivity (ohm)	0.0183		Resistivity (ohm)	0.0183
Current	#N/A		Imp	8.5
Power factor	1		Voltage at max power	244.8
Voltage (RMS)	230		Permitted voltage drop	3.0%
Permitted voltage rise	1%
Minimum CSA for 1% drop	#N/A	mm2	Minimum CSA for 3% drop	0.34	mm2

Chosen CSA for AC cabling	4	mm2	Chosen CSA for DC cabling	4	mm2
AC drop for chosen CSA	#N/A		DC drop for chosen CSA	0.254%

Total voltage drop loss	#N/A

## DC isolators
DC isolator rating

Array configuration
String 1	8
String 2
String 3
String 4

PV max array voltage	334.9
Minimum current rating	11.3

## Yield
Yield

Tilt and orientation
Melb 20/310

Array power	2.08	kW

Daily horiz irradiation	4.1	PSH
Shading loss	0.95
Tilt and orientation	#N/A
Annual irradiation	#N/A	kWh/m2/year

Manuf tolerance	1
Temperature loss	.922
Soiling loss	0.95
Voltage drop	#N/A
Inverter loss	#N/A
System efficiency	#N/A

Annual yield	#N/A	kWh/year

## Modules
Modules

Module model	Pmax	Vmp	Imp	Voc	Isc (A)	Eff %	Fuse (A)	Pmax	Voc	Vmp	Isc	Manuf. Tolerance	Height	Width
CS6P-235P	235	29.8	7.9	36.9	8.46	14.61	15	-0.43%	-0.34%	-0.43%	0.07%	0.00%	1638	982
CS6P-240P	240	29.9	8.03	37	8.59	14.92	15	-0.43%	-0.34%	-0.43%	0.07%	0.00%	1638	982
CS6P-245P	245	30	8.17	37.1	8.74	15.23	15	-0.43%	-0.34%	-0.43%	0.07%	0.00%	1638	982
CS6P-250P	250	30.1	8.3	37.2	8.87	15.54	15	-0.43%	-0.34%	-0.43%	0.07%	0.00%	1638	982
CS6P-255P	255	30.2	8.43	37.4	9	15.85	15	-0.43%	-0.34%	-0.43%	0.07%	0.00%	1638	982
STP270S-20	270	30.8	8.77	38.3	9.28	16.6	20	-0.44%	-0.34%	-0.44%	0.06%	0.00%	1640	992
STP275S-20	275	31.1	8.85	38.5	9.34	16.9	20	-0.44%	-0.34%	-0.44%	0.06%	0.00%	1640	992
TSM-250	250	30.3	8.27	38	8.79	15.3	15	-0.41%	-0.32%	-0.41%	0.05%	0.00%	1650	941
TSM-255	255	30.5	8.37	38.1	8.88	15.6	15	-0.41%	-0.32%	-0.41%	0.05%	0.00%	1650	941
TSM-260	260	30.6	8.5	38.2	9	15.9	15	-0.41%	-0.32%	-0.41%	0.05%	0.00%	1650	941
TSM-265	265	31	8.55	38.4	9.1	16.2	15	-0.41%	-0.32%	-0.41%	0.05%	0.00%	1650	941
YL250C	250	30.5	8.2	38.1	8.71	15.3	20	-0.42%	-0.31%	-0.41%	0.04%	0.00%	1650	990
YL255C	255	30.6	8.33	38.3	8.85	15.6	20	-0.42%	-0.31%	-0.41%	0.04%	0.00%	1650	990
YL260C	260	30.8	8.46	38.6	8.91	15.9	20	-0.42%	-0.31%	-0.41%	0.04%	0.00%	1650	990
YL265C	265	31	8.55	39	8.93	16.2	20	-0.42%	-0.31%	-0.41%	0.04%	0.00%	1650	990
YL270C	270	31.1	8.68	39	9.06	16.5	20	-0.42%	-0.31%	-0.41%	0.04%	0.00%	1650	990
YL275C	275	30.8	8.94	38.6	9.55	16.8	20	-0.42%	-0.31%	-0.41%	0.04%	0.00%	1650	990
YL280C	280	31.1	9.01	38.9	9.61	17.1	20	-0.42%	-0.31%	-0.41%	0.04%	0.00%	1650	990

## Inverters
Inverters

Model	Min MPPT voltage (V)	Max MPPT voltage (V)	Max input voltage (V)	Max input current (A)	Max DC power (W)	Efficiency	Max output current (A)
SMA SB5000TL	175	500	750	15	5250	0.97	22
SMA SB15000TL	240	800	1000	33	27000	0.98	29
SMA SB20000TL	320	800	1000	33	36000	0.98	29
SMA SB25000TL	390	800	1000	33	45000	0.98	36.2

## Temperatures
Temperature Data

	Min cell temp	Avg ambient	Max cell temp
Sydney	0	23	70
Melbourne	-5	19	75

## Radiation
Daily Irradiation on a Horizontal Plane (by month)

	Sydney	Melbourne		Syd 20 / 20	Melb 20 / 310
January	6.5	6.7		100	102
February	5.7	5.9		105	106
March	4.7	4.5		113	112
April	3.6	3.2		124	118
May	2.7	2.1		137	126
June	2.4	1.7		142	131
July	2.6	1.9		141	128
August	3.4	2.6		130	121
September	4.6	3.6		117	114
October	5.6	4.8		107	108
November	6.2	5.9		101	103
December	6.6	6.5		98	100
Average	4.6	4.1		118	114

## License
    This program is free software: you can redistribute it and/or modify
    it under the terms of the GNU General Public License as published by
    the Free Software Foundation, either version 3 of the License, or
    (at your option) any later version.

    This program is distributed in the hope that it will be useful,
    but WITHOUT ANY WARRANTY; without even the implied warranty of
    MERCHANTABILITY or FITNESS FOR A PARTICULAR PURPOSE. See the
    GNU General Public License for more details.

    You should have received a copy of the GNU General Public License
    along with this program. If not, see <https://www.gnu.org/licenses/>.