## System_Design
	Copyright Global Energy Training Solutions / Please see licence on page 4 / Feedback and suggestions welcome: ben.murphy@gets.edu.au					Colour legend
				Input data
				Answers

Matching panels to inverters

Panel Specs				Inverter Specs				Temperature for region
VOC	40.1	V		Vmax of inverter (or V limit)	600	V		Hotest day (Tmax)	45	ºC
VMPP	32.6	V		Vmin of inverter	80	V		Coldest morning (TMIN)	-10	ºC
ISC	9.72	A		MPPT Voltage maximum	600	V		Average max temp (TA.DAY)	20	ºC
IMPP	9.21	A		MPPT Voltage minimum	80	V
Temperature coefficent for VOC	-0.29	%/ºC		MPPT maximum efficiency	310	V		Minimum rating for isolators and cables
Temperature coefficent for IMPP	0.05	%/ºC		Imax of inverter MPPT	27	A		ISC	9.72	A
Temperature coefficent for PMAX	-0.39	%/ºC		Maximum AC current output of inverter	21.7	A		Fomula	1.25	x
Panel Watts	300	W		Maximum output AC power of inverter	5	kW		Minimum rating for Iso’s and cables	12.15	A
Manufacturers tolerance	3	%		Inverter efficiency	97	%

VMAX				VMIN				IMAX
Formula: VMAX_OC = VOC_STC + [γv x (TMIN - TSTC)]				Formula: VMPP_CELL.EFF = VMP_STC + [ γv x (TCELL_EFF – TSTC)]				Formula: ISC_CELL.EFF = ISC_STC + [ γI x (TCELL_EFF – TSTC)]
VOC of Panel (VOC_STC)	40.1	V		VMPP of Panel (VMPP_CELL.EFF)	32.6	V		ISC of Panel (ISC_CELL.EFF)	9.72	A
Temp coefficient of panel (γv)	-0.11629	V/ºC		Temp coefficient of panel (γv)	-0.11629	V/ºC		Temp coefficient of panel (γI)	0.00486	A/ºC
Coldest morning (TMIN)	-10	ºC		Hottest day + 250 (TCELL_EFFx)	70	ºC		Hottest day + 250 (TCELL_EFFx)	70	ºC
Part of Formula (TSTC)	25	ºC		Part of Formula (TSTC)	25	ºC		Part of Formula (TSTC)	25	ºC
VMAX per panel (VMAX_OC)	44.170	V		VMIN per panel (VMPP_CELL.EFF):	27.367	V		IMAX per string (ISC_CELL.EFF)	9.939	A
VMAX of inverter	600	V		VMIN of inverter	80	V		IMAX of inverter MPPT	27	A
Maximum panels per string	13	Panels		Minimum panels per string	3	Panels		Maximum strings per MPPT	2	Strings
	(Rounded down)				(Rounded up)				(Rounded down)

MPPT VMAX				MPPT VMIN				MPPT VAVE
Formula: VMAX_OC = VMPP + [γv x (TMIN - TSTC)]				Formula: VMPP = VMPP + [ γv x (TCELL_EFF – TSTC)]				Formula: VMPP = VMPP + [ γv x (TCELL_EFF – TSTC)]
VMPP of Panel (VMPP STC)	32.6	V		VMPP of Panel (VMPP_STC)	32.6	V		VMPP of Panel (VMPP_STC)	32.6	V
Temp coefficient of panel (γv)	-0.15639	V/ºC		Temp coefficient of panel (γv)	-0.15639	V/ºC		Temp coefficient of panel (γv)	-0.15639	V/ºC
Coldest morning (TMIN)	-10	ºC		Hottest day + 250 (TCELL_EFFx)	70	ºC		Average day + 250 (TCELL_EFFx)	45	ºC
Part of Formula (TSTC)	25	ºC		Part of Formula (TSTC)	25	ºC		Part of Formula (TSTC)	25	ºC
VMAX per panel (VMAX_OC)	38.074	V		VMIN per panel (VMPP_CELL.EFF):	25.562	V		V per panel (VMPP_CELL.EFF):	29.472	V
MPPT VMAX of inverter	600	V		MPPT VMAinof inverter	80	V		MPPT VAVE 8 panels	200.0	V
Maximum panels per string	15	Panels		Maximum panels per string	4	Panels		MPPT VAVE 9 panels	225.0	V
	(Rounded down)				(Rounded up)			MPPT VAVE 10 panels	294.7	V
				MPPT VAVE 11 panels	324.2	V
				MPPT VAVE 12 panels	353.7	V
				MPPT VAVE 13 panels	383.1	V
				MPPT VAVE 14 panels	412.6	V
				MPPT VAVE 15 panels	442.1	V
				MPPT VAVE 16 panels	471.6	V
				MPPT VAVE 17 panels	501.0	V
				MPPT VAVE 18 panels	530.5	V
				MPPT VAVE 19 panels	560.0	V
				MPPT VAVE 20 panels	589.4	V
				MPPT maximum efficiency	310	V
				Select close to or slightly higher

## Losses_&_Energy_yield
	Copyright Global Energy Training Solutions / Please see licence on page 4 / Feedback and suggestions welcome: ben.murphy@gets.edu.au					Colour legend
				Input data
				Answers

Losses & energy yield

VD DC					VD AC 1 Phase or 3 phase (as selected above)
Formula: L x I x Vc x 1.155 / 1000					Formula: L x I x Vc x 1.155 / 1000
Panels (string)	11					Select either 230V or 400V	230	V
L (Meters)	15.5	m					L (Meters)	6	m
IMPP (Amps)	9.21	A					I (Amps)	21.7	A
Vc (mV/Am) at 750 – Single-core / AS/NZS 3008, Table 47, Column 6	4mm2	6mm2	10mm2	16mm2	25mm2		Vc (mV/Am) at 750 – Multicore / AS/NZS 3008, Table 42, Column 6	2.5mm2	4mm2	6mm2	10mm2	16mm2	25mm2	35mm2	50mm2
	10.4	6.96	4.03	2.56	1.66			15.6	9.71	6.49	3.86	2.43	1.54	1.11	0.829
1.155	1.155					1.155	1.155
1000	1000					1000	1000
VD (Actual voltage drop in volts)	1.71	1.15	0.66	0.42	0.27		VD (Actual voltage drop in volts)	2.35	1.46	0.98	0.58	0.37	0.23	0.17	0.12
VMPP	32.6	V					Supply voltage	230	V
String voltage	358.6	V					Total losses	1.02%	0.63%	0.42%	0.25%	0.16%	0.10%	0.07%	0.05%
Total losses	0.48%	0.32%	0.19%	0.12%	0.08%		Efficiency factor	0.990	0.994	0.996	0.997	0.998	0.999	0.999	0.999
Efficiency factor	0.995	0.997	0.998	0.999	0.999		Note: Also used to calculate voltage rise

Total efficiency factor (losses)					PMAX
Total efficiency factor = Htilt x fshade x ftemp x fdirt x fman x ηinv x ηVD_DC x ηVD_AC					Modified formula: ƒTEMP = 1 + [ γ × TA.DAY)
Effect of orientation and tilt			Htilt	0.950			Part of formula	1
Solar irradiation loss (shading)			fshade	0.950			Temp coefficient of panel (γ)	-0.0039	%/ºC
De-rating due to temperature			ftemp	0.922			Average max temp (TA.DAY)	20	ºC
De-rating due to dirt			fdirt	0.950			Efficiency factor	0.922
Manufacturer’s stated manufacturing tolerance			fman	0.970
Inverter efficiency			ηinv	0.970			AC output after losses In kW
DC cable loss between the array and the inverter			ηVD_DC	0.995			Panel wattage	300	W
AC cable loss between the inverter and energy meter			ηVD_AC	0.994			Number of panels	22
			Total	0.736			DC Power	6.60	kW
				Losses	0.736
				AC Power	4.854	kW

				Panels not less than 75% of Inverter check
				AC power from inverter	5.00	kW
				DC power form panels	6.60	kW
				% panels of inverter	75.76	%
				Must be higher than 75%

## Payback Calcs
		Copyright Global Energy Training Solutions / Please see licence on page 4 / Feedback and suggestions welcome: ben.murphy@gets.edu.au					Colour legend
				Input data
				Answers

Annual yield in kW.h					Install cost (Labour + materials)
DC power In kW	Losses	AC Power in KW	PSH	Days	kW.h per year				Labour (consider all costs)			$2,000.00
				Panels (get quote)			$4,000.00
6.60	0.736	4.854	4.9	365.25	8688.16				Inverter (get quote)			$1,300.00
				Rail and sundries (get quote)			$1,000.00
				Certificate of Electrical Safety			$249.00
Consumed	Buy price 2018/2019	Annual savings not bought from retailer	Exported	Sell price / 2018/2019	Earnings per year	Total $ per Annum	Pay back period (years):		Total			$8,549.00	*Note 1
				STCs rebate
				STCs (look up)			109	*Note 2
	$0.25			$0.11					Price per STC (look up)			-$36.70	*Note 3
0.00%	$0.25	$0.00	100.00%	$0.11	$955.70	$955.70	6.5		Total			-$4,000.30
10.00%	$0.25	$217.52	90.00%	$0.11	$860.13	$1,077.64	5.7		Install cost less STCs
20.00%	$0.25	$435.03	80.00%	$0.11	$764.56	$1,199.59	5.1		Ex GST			$4,548.70
30.00%	$0.25	$652.55	70.00%	$0.11	$668.99	$1,321.54	4.7		Inc GST			$5,003.57	*Note 4
40.00%	$0.25	$870.07	60.00%	$0.11	$573.42	$1,443.49	4.3		Maintenance over 10 yrs
50.00%	$0.25	$1,087.58	50.00%	$0.11	$477.85	$1,565.43	3.9		Anti islanding test - 5 yr			$180.00
60.00%	$0.25	$1,305.10	40.00%	$0.11	$382.28	$1,687.38	3.7		Anti islanding test - 10 yr			$180.00
70.00%	$0.25	$1,522.62	30.00%	$0.11	$286.71	$1,809.33	3.4		Cleaning - 3 yr			$270.00
80.00%	$0.25	$1,740.13	20.00%	$0.11	$191.14	$1,931.27	3.2		Cleaning - 6 yr			$270.00
90.00%	$0.25	$1,957.65	10.00%	$0.11	$95.57	$2,053.22	3.0		Cleaning - 9 yr			$270.00
100.00%	$0.25	$2,175.17	0.00%	$0.11	$0.00	$2,175.17	2.8		Total			$1,170.00	*Note 1
Does not include a margin for error, however also doesn’t include electricity price increases.					Total over 10 yrs (Install + Maintenance)
				Total			$6,173.57

Note 1: Rough estimates only
Note 2: 109 = 6.6kw system in Canberra in 2019. Calculate here: https://www.rec-registry.gov.au/rec-registry/app/calculators/sgu-stc-calculator
Note 3: Changes as per market
Note 4: Does not include switchboard upgrade, 2 story roof or split systems

## Licence
    This program is free software: you can redistribute it and/or modify
    it under the terms of the GNU General Public License as published by
    the Free Software Foundation, either version 3 of the License, or
    (at your option) any later version.

    This program is distributed in the hope that it will be useful,
    but WITHOUT ANY WARRANTY; without even the implied warranty of
    MERCHANTABILITY or FITNESS FOR A PARTICULAR PURPOSE. See the
    GNU General Public License for more details.

    You should have received a copy of the GNU General Public License
    along with this program. If not, see <https://www.gnu.org/licenses/>.