## Sheet1
	Copyright Global Energy Training Solutions / Please see licence on next page / Feedback and suggestions welcome: ben.murphy@gets.edu.au					Colour legend
				Input data
				Answers

Matching panels to inverters + energy yield

Panel Specs				Inverter Specs				VD DC
VOC	40.1	V		Vmax of inverter (or V limit)	600	V		Formula: L x I x Vc x 1.155 / 1000
VMPP	32.6	V		Vmin of inverter	80	V		Panels (string)	11
ISC	9.72	A		MPPT Voltage maximum	600	V		L (Meters)	15.5	m
IMPP	9.21	A		MPPT Voltage minimum	80	V		I (Amps)	9.21	A
Temperature coefficent for VOC	-0.29	%/ºC		MPPT maximum efficiency	310	V		Vc (mV/Am) at 900 – Multicore / AS/NZS 3008, Table 42, Column 8	4mm2	6mm2	10mm2	16mm2	25mm2
Temperature coefficent for IMPP	0.05	%/ºC		Imax of inverter MPPT	27	A			10.2	6.8	4.05	2.55	1.61
Temperature coefficent for PMAX	-0.39	%/ºC		Maximum AC current output of inverter	21.7	A		1.155	1.155
Panel Watts	300	W		Maximum output AC power of inverter	5	kW		1000	1000
				VD (Actual voltage drop in volts)	1.68	1.12	0.67	0.42	0.27
Temperature for region					VMPP	32.6	V
Hotest day (Tmax)	45	ºC					String voltage	358.6	V
Coldest morning (TMIN)	-10	ºC					Total losses	0.47%	0.31%	0.19%	0.12%	0.07%
Average max temp (TA.DAY)	20	ºC					Efficiency factor	0.995	0.997	0.998	0.999	0.999
				MPPT VMAX
VMAX				Formula: VMAX_OC = VMPP + [γv x (TMIN - TSTC)]				VD AC 1 Phase or 3 phase (as selected above)
Formula: VMAX_OC = VOC_STC + [γv x (TMIN - TSTC)]				VMPP of Panel (VMPP STC)	32.6	V		Formula: L x I x Vc x 1.155 / 1000
VOC of Panel (VOC_STC)	40.1	V		Temp coefficient of panel (γv)	-0.15639	V/ºC		Select either 230V or 400V	230	V
Temp coefficient of panel (γv)	-0.11629	V/ºC		Coldest morning (TMIN)	-10	ºC		L (Meters)	6	m
Coldest morning (TMIN)	-10	ºC		Part of Formula (TSTC)	25	ºC		I (Amps)	21.7	A
Part of Formula (TSTC)	25	ºC		VMAX per panel (VMAX_OC)	38.074	V		Vc (mV/Am) at 750 – Multicore / AS/NZS 3008, Table 42, Column 6	2.5mm2	4mm2	6mm2	10mm2	16mm2	25mm2	50mm2	50mm2
VMAX per panel (VMAX_OC)	44.170	V		MPPT VMAX of inverter	600	V			15.6	9.71	6.49	3.86	2.43	1.54	1.11	0.829
VMAX of inverter	600	V		Maximum numbers of panels per string	15.8	Panels		1.155	1.155
Maximum numbers of panels per string	13.6	Panels			Round down			1000	1000
	Round down					VD (Actual voltage drop in volts)	2.35	1.46	0.98	0.58	0.37	0.23	0.17	0.12
				MPPT VMIN				Supply voltage	230	V
VMIN				Formula: VMPP = VMPP + [ γv x (TCELL_EFF – TSTC)]				Total losses	1.02%	0.63%	0.42%	0.25%	0.16%	0.10%	0.07%	0.05%
Formula: VMPP_CELL.EFF = VMP_STC + [ γv x (TCELL_EFF – TSTC)]				VMPP of Panel (VMPP_STC)	32.6	V		Efficiency factor	0.990	0.994	0.996	0.997	0.998	0.999	0.999	0.999
VMPP of Panel (VMPP_CELL.EFF)	32.6	V		Temp coefficient of panel (γv)	-0.15639	V/ºC		Note: Also used to calculate voltage rise
Temp coefficient of panel (γv)	-0.11629	V/ºC		Hottest day + 250 (TCELL_EFFx)	70	ºC
Hottest day + 250 (TCELL_EFFx)	70	ºC		Part of Formula (TSTC)	25	ºC		PMAX
Part of Formula (TSTC)	25	ºC		VMIN per panel (VMPP_CELL.EFF):	25.562	V		Modified formula: ƒTEMP = 1 + [ γ × TA.DAY)
VMIN per panel (VMPP_CELL.EFF):	27.367	V		MPPT VMAinof inverter	80	V		Part of formula	1
VMIN of inverter	80	V		Maximum numbers of panels per string	3.1	Panels		Temp coefficient of panel (γ)	-0.0039	%/ºC
Minimum numbers of panels per string	2.9	Panels			Round up			Average max temp (TA.DAY)	20	ºC
	Round up					Efficiency factor	0.922
				MPPT VAVE
IMAX				Formula: VMPP = VMPP + [ γv x (TCELL_EFF – TSTC)]				Total efficiency factor (losses)
Formula: ISC_CELL.EFF = ISC_STC + [ γI x (TCELL_EFF – TSTC)]				VMPP of Panel (VMPP_STC)	32.6	V		Total efficiency factor = Htilt x fshade x ftemp x fdirt x fman x ηinv x ηVD_DC x ηVD_AC
ISC of Panel (ISC_CELL.EFF)	9.72	V		Temp coefficient of panel (γv)	-0.15639	V/ºC		Effect of orientation and tilt			Htilt	0.950
Temp coefficient of panel (γI)	0.00486	A/ºC		Average day + 250 (TCELL_EFFx)	45	ºC		Solar irradiation loss (shading)			fshade	0.950
Hottest day + 250 (TCELL_EFFx)	70	ºC		Part of Formula (TSTC)	25	ºC		De-rating due to temperature			ftemp	0.922
Part of Formula (TSTC)	25	ºC		V per panel (VMPP_CELL.EFF):	29.472	V		De-rating due to dirt			fdirt	0.950
IMAX per string (ISC_CELL.EFF)	9.939	V		MPPT VAVE 9 panels	225.0	V		Manufacturer’s stated manufacturing tolerance			fman	0.970
IMAX of inverter MPPT	27	V		MPPT VAVE 10 panels	294.7	V		Inverter efficiency			ηinv	0.970
Maximum strings per MPPT	2.7	Strings		MPPT VAVE 11 panels	324.2	V		DC cable loss between the array and the inverter			ηVD_DC	0.995
	Round down			MPPT VAVE 12 panels	353.7	V		AC cable loss between the inverter and energy meter			ηVD_AC	0.922
				MPPT VAVE 13 panels	383.1	V					Total	0.683
				MPPT VAVE 14 panels	412.6	V
				MPPT maximum efficiency	310	V		AC output after losses In kW
				Select higher			Panel wattage	300	W
				Number of panels	22
				DC Power	6.60	kW
				Losses	0.683
				AC Power	4.505	kW

				Panels not less than 75% of Inverter check
				AC power from inverter	5.00	kW
				DC power form panels	6.60	kW
				% panels of inverter	75.76	%
				Must be higher than 75%

## Licence
    This program is free software: you can redistribute it and/or modify
    it under the terms of the GNU General Public License as published by
    the Free Software Foundation, either version 3 of the License, or
    (at your option) any later version.

    This program is distributed in the hope that it will be useful,
    but WITHOUT ANY WARRANTY; without even the implied warranty of
    MERCHANTABILITY or FITNESS FOR A PARTICULAR PURPOSE. See the
    GNU General Public License for more details.

    You should have received a copy of the GNU General Public License
    along with this program. If not, see <https://www.gnu.org/licenses/>.